## Slide 1
Water quality modelling of Free Water Surface Tancat de la Pipa Wetland for urban runoff mitigation optimization
Martínez-Biosca, A1. *, Hernández-Crespo, C.1, Andrés-Doménech, I.1, Rodrigo-Santamalia, M.E.2 , García-Haba, E. 1, Calzadilla-Cabrera, D. 1, Martín M1
1 Instituto de Ingeniería del Agua y Medio Ambiente - UPV, Valencia, Spain,
2 Instituto Agroforestal Mediterráneo - UPV, Valencia, Spain

## Slide 2
INTRODUCTION
MATERIAL AND METHODS
RESULTS
  MONITORING PERIOD
  WATER QUALITY
  WATER QUALITY MODELLING
  FUTURE LINES
CONCLUSIONS

## Slide 3
1. INTRODUCTION
Location in the north of the Albufera Natural Park
The CURRENT CHALLENGE is focused on combined sewer overflows (CSOs), especially with the new version of EU treatment Directive
Wastewater discharges were eliminated
ALBUFERA
LAKE
Tancat de la Pipa
The urban, agricultural, and industrial growth of Valencia and nearby towns since the 1970s.
Albufera Lake has suffered significant anthropic pressures, including urban and industrial wastewater discharges, as well as agricultural and urban runoff
HYPEREUTROPHIC STATE
VALENCIA

## Slide 4
1. INTRODUCTION
ALBUFERA LAKE
FG1
FG2
FG3
fp1
fp2
fp3
F4-SL
F4-SC
BP
PC
Reserve Lagoon
Educative
Lagoon
F4-SM
ALBUFERA LAKE
Catarroja
RICE
PADDIES
Barranco del
Poyo (BP)
Acequia del puerto
de Catarroja (PC)
2 km
Commercial and industry areas
Tancat de la Pipa
Albal
Silla
Overflow points
Sector B: FWSCW: Divided into 3 independent sub-sectors (FP, FG, and F4)
Sector C: Educative and Reserve Lagoons
Sector D: Sinkhole (artificial spring)
Sinkhole
5.5 km
WEST COLLECTOR

## Slide 5
OBJECTIVES:
Quantify the impact of combined sewer overflows (CSOs) on Albufera lake in terms of pollutant concentrations, using samples taken at TPCW inflow points.
Evaluate the role of large constructed wetlands, not specifically designed for this, in mitigating urban and agriculture runoff.
Develop and calibrate a water quality model to optimize the operation and design of constructed and restored wetlands.

## Slide 6
Sampling methods:
Autosamplers (Hach, 24-bottle capacity) + Grab samples collected at 6 points within TPCW, twice a day, for up to one week post-event.
2. MATERIAL AND METHODS
Measured Variables:
Physicochemical: COD, nitrogen species (TN, N-NH4+, N-NO2-, N-NO3-), TP and P-PO43-, OD, turbidity and conductivity.
Selected pollutants: Pesticides and emerging contaminants (e.g., Ibuprofen, Paracetamol, Tebuconazole).
Modelling approach:
Initial phase: simple CSTRs for each wetland/lagoon in spreadsheets
Second phase: develop a full FWSCW model in COMSOL Multiphysics® software.
Monitoring points at TPCW
PC
BP
LE-1
LR-1
LE-2
LR-2
ALBUFERA
LAKE

## Slide 7
3. RESULTS - MONITORING PERIOD
Monitoring period | Nº of Rainfalls | Total Depth (mm) | i-max (mm/h)
1 | 2 | 48.6 | 20.0
2 | 8 | 117.4 | 37.0
3 | 2 | 123.0 | 68.8
4 | 1 | 14.4 | 2.8
5 | 1 | 14.2 | 6.0
6 | 1 | 4.4 | 2.2
7 | 2 | 24.8 | 9.4
8 | 1 | 18.6 | 4.5
9 | 2 | 45.0 | 11.8
10 | 3 | 72.2 | 10.6
The monitoring period: February 2023 – November 2024 (keep working)
Total rainfalls: 23
Valencia has an average of 27.2 rainfalls per year

## Slide 8
3. RESULTS – WATER QUALITY
Event Monitored: 2nd (May 2023), Monitoring Duration: 21 days, Total Rainfalls: 8, Total Depth: 117.4 mm, (i-max): 37 mm/h
0.65 mg N-NH4+/l
Ammonia and nitrites concentrations in TPCW during the rain event in May 2023. Dashed line indicates historical average inflow concentration at PC 2009-23 (n=211).
3.01 mg N-NO3-/l
With each rainfall, the concentration increases, reaching peaks of 6.3 and 2.5 times.
At the wetland’s outlet  The peaks are reduced by almost 80% as the water flows through the Tancat.
The EMC at the Educational Lagoon is close to their historical average  TPCW manages the runoff effectively.

## Slide 9
3. RESULTS – WATER QUALITY
0.35 mg P/l
TP concentrations in TPCW during the rain event in May 2023. Dashed line indicates mean PC inflow concentration 2009-23 (n=211).
0.5 mg P/l
Black dashed line represents the updated value of the European Directive for the TP discharge limit 0.5 mg P/l (>150.000 p.e.).
Event Monitored: 2nd (May 2023), Monitoring Duration: 21 days, Total Rainfalls: 8, Total Depth: 117.4 mm, (i-max): 37 mm/h
The same trend is observed: after each rainfall, the concentration increases  3 times their historical average.
At the wetland outflows, the TP concentration is below 0.5 mg P/l.
At the Educational Lagoon outflow, the TP concentration decreases even further.

## Slide 10
Basic model (1 reactor)  Understand the wetland and identify key points for a future model
No tracer experiments in TPCW (NATURAL PARK): CONDUCTIVITY  Learn about hydraulics
System balance: EVAPORATION is an output and RAINFALL is an input
Vegetation has not been considered in the model at this stage
Qin:30 l/s
Qout:30 l/s
h: 0.2 - 0.3 m
S: 2.59 ha
CSTR (1 reactor)
PC
F4
3. RESULTS – WATER QUALITY MODELLING
HRT:1.5 d
LE-1
Spreadsheets
1st event February, 2023

## Slide 11
Qin:30 l/s
Qout:30 l/s
h:0.2 - 0.3 m
S:2.59 ha
CSTR (1 reactor)
3. RESULTS – WATER QUALITY MODELLING
Qin:30 l/s
Qout:30 l/s
h: 0.2 - 0.3 m
S:2.59 ha
CSTR (1 reactor)
HRT:1.5 d
R2:0.85
RMSE:139.5
R2:0.85
RMSE:102.4
15
15
Molecular diffusion
COMSOL Multiphysics®
Molecular diffusion
Molecular diffusion
Cwater
Csed
Source | Type | D (m²/s)
Surface water quality modeling (Chapra, 2008) | Natural Waters and sediments | 10-8 - 10-9 10-9 - 10-12
Environmental Modeling Fate and Transport of Pollutants in Water, Air, and Soil (Schnoor, J. L. 1996) | Lakes (water -sediments) | 10-9 - 10-14
Gargallo Bellés, S. (2017) | TPCW | 2.0·10-9
Current study (2024) | TPCW | 3.0 - 5.0·10-8

## Slide 12
Qin:30 l/s
Qout:30 l/s
3. RESULTS – WATER QUALITY MODELLING
Q1,in≈ 0.49 Q1,out
Q2,in≈ 0.40 Q2,out
Q3,in≈ 0.11 Q,3out
15
R2:0.87
RMSE:57.2
15
R2:0.90
RMSE:39.2
Q1,in
Q2,in
Q3,in
Q1,out
Q2,out
Q3,out
COMSOL Multiphysics®
Molecular diffusion
Molecular diffusion
h: 0.2 - 0.3 m
S:2.59 ha
CSTR (10 reactors, 1 line)
h: 0.2 - 0.3 m
S:≈ 0.86 ha each line
CSTR (10 reactors, 3 lines)

## Slide 13
3. RESULTS – WATER QUALITY MODELLING
R2: 0.78
RMSE:60.1
mg N-NH4+/l
mg TSS/l
1st event, February 2023
Total Suspended Solids (TSS)
Ammonium (N-NH4+)
: 0.15 md-1
0.1 d-1
R2: 0.91
RMSE:53.2
15
15

## Slide 14
3. RESULTS – WATER QUALITY MODELLING
4th event, January 2024
7th event, June 2024
Diffusion term
Flow distribution
Diffusion Term
Flow distribution
Q1,in
Q2,in
Q3,in
Q1,out
Q2,out
Q3,out
h: 0.2 - 0.3 m
S:≈ 0.86 ha each line
CSTR (10 reactors, 3 lines)
R2: 0.85
RMSE:37
R2: 0.70
RMSE:176
R2:0.89
RMSE:206
R2: 0.91
RMSE:106

## Slide 15
3. RESULTS – FUTURE LINES
Developing a CFD Model for subsector F4 in COMSOL Multiphysics®
h: 0.3 m
S≈ 0.86 ha
h: 0.3 m
S≈ 0.86 ha
h: 0.3 m
S≈ 0.86 ha
Q1,in
Q2,in
Q3,in
Q1,out
Q2,out
Q3,out
Basic models to understand the F4 sub-sector.
Our simulations show good results, demonstrating the value of these models
Limited in adding processes or simulating management operations.
Complete the model by including the educational lagoon
Incorporating vegetation to study its effect on flow dynamics
Ultimate goal: to develop a full model for the TPCW
Example of geometry design for a CFD model of subsector F4
INITIAL STEPS
CURRENT WORK
NEXT STEPS

## Slide 16
Preliminary results confirm that pollutant loads from CSOs into Albufera Lake significantly increase concentrations in the BP and PC channels, reaching peaks higher than usual.
4. CONCLUSIONS
FWSCWs are effective at reducing pollutant peaks without compromising their functionality. In addition, they are able to mitigate urban and agricultural runoff.
The TPCW provides reasonable results with a basic model, tanks in series perform much better, although CFD are the best option for what we are looking for.
Mathematical models will help us to optimize the maximum inflow that the wetland is able to manage, without compromising standard quality at the outlet.

## Slide 17
The project TED2021-130567B-I00 RAINWETPIPA is financed by EU-Next Generation funds. Ministry of Science, Innovation and Universities. Government of Spain.
Acknowledgments
Thank you very much for your attention